SL 3503.1 LED CG-S white

Pos.    )		ea.

Safety luminaire in LED technology with symmetric light distribution for recessed installation in keeping with German / European standards DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for operation on safety illumination systems in keeping with German / European standards DIN VDE 0100-718, DIN EN 50172 and E DIN VDE 0108-100; developed, manufactured and tested in keeping with ISO 9001.

Round Bezel with 80 mm diameter, laquered white (similar to RAL 9010). Installation of the luminaire without use of tools by clamping springs for ceiling thicknesses of up to 20 mm. Drill hole diameter 68 mm. Low installation depth of only 36 mm. LED converter in a separate housing made of plastics with throughwiring terminals and strain relief. Required depth for entering the ceiling only 100mm.

Symmetric white beam light distribution for enlarged spacing with mounting heights of

up to 7.5 m. Maximum spacing between luminaires:

> 10 m as from 3 m mounting height up to 13 m at 6 to 7.5 m height

(basis of calculation at least 1 lx in centre of escape route - maintenance factor WF = 0.8)

Light source: 3 x high efficient, white HighPower LEDs 1.1 W with a service life of 50.000 h  on account of optimised LED operating conditions.

Special LED converter with integrated monitoring module for single luminaire monitoring

with twenty addresses for fault and performance monitoring (CEWA GUARD technology).

Freely programmable mixed operation of the connection systems (Maintained light, non maintained light and switched maintained light) within a circuit without additional data or actuating cables to the luminaires is possible in combination with suitable safety lighting system with STAR technology.

Luminous flux at the end of the rated service time:	100%

Housing material: 					aluminium, steel, PC

Housing colour: 					white (similar to RAL 9010)

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		19 mA

Power consumption including LED supply

(apparent power / effective power): 			7.6 VA / 4.4 W.

Class of protection:					II

Type of protection					IP 20

Permissible ambient temperature: 			-20° Celsius to +40° Celsius

Dimensions (mm) :					D = 80 H = 38

Housing for LED converter:

L = (132 + 85), H = 26, T = 47 (bent construction)

Dimensions - ceiling cutout (mm):			Diameter = 68 mm

Type: 3503.1 LED CG-S white

Make: CEAG

SL 3503.1 LED CG-S stainless steel

Pos.    )		ea.

Safety luminaire in LED technology with symmetric light distribution for recessed installation in keeping with German / European standards DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for operation on safety illumination systems in keeping with German / European standards DIN VDE 0100-718, DIN EN 50172 and E DIN VDE 0108-100; developed, manufactured and tested in keeping with ISO 9001.

Round Bezel with 80 mm diameter, made of brushed stainless steel. Installation of the luminaire without use of tools by clamping springs for ceiling thicknesses of up to 20 mm. Drill hole diameter 68 mm. Low installation depth of only 36 mm. LED converter in a separate housing made of plastics with throughwiring terminals and strain relief. Required depth for entering the ceiling only 100mm.

Symmetric white beam light distribution for enlarged spacing with mounting heights of

up to 7.5 m. Maximum spacing between luminaires:

> 10 m as from 3 m mounting height up to 13 m at 6 to 7.5 m height

(basis of calculation at least 1 lx in centre of escape route - maintenance factor WF = 0.8)

Light source: 3 x high efficient, white HighPower LEDs 1.1 W with a service life of 50.000 h on account of optimised LED operating conditions.

Special LED converter with integrated monitoring module for single luminaire monitoring

with twenty addresses for fault and performance monitoring (CEWA GUARD technology).

Freely programmable mixed operation of the connection systems (Maintained light, non maintained light and switched maintained light) within a circuit without additional data or actuating cables to the luminaires is possible in combination with suitable safety lighting system with STAR technology.

Luminous flux at the end of the rated service time:	100%

Housing material: 					aluminium, steel, PC

Housing colour: 					stainless steel brushed

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		19 mA

Power consumption including LED supply

(apparent power / effective power): 			7.6 VA / 4.4 W.

Class of protection:					II

Type of protection					IP 20

Permissible ambient temperature: 			-20° Celsius to +40° Celsius

Dimensions (mm) :					D = 80 H = 38

Housing for LED converter:

L = (132 + 85), H = 26, T = 47 (bent construction)

Dimensions - ceiling cutout (mm):			Diameter = 68 mm

Type: 3503.1 LED CG-S stainless steel

Make: CEAG

SL 3504.1 LED CG-S white

Pos.    )		ea.

Safety luminaire in LED technology with symmetric light distribution for recessed installation in keeping with German / European standards DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for operation on safety illumination systems in keeping with German / European standards DIN VDE 0100-718, DIN EN 50172 and E DIN VDE 0108-100; developed, manufactured and tested in keeping with ISO 9001.

Round Bezel with 80 mm diameter, laquered white (similar to RAL 9010). Installation of the luminaire without use of tools by clamping springs for ceiling thicknesses of up to 20 mm. Drill hole diameter 68 mm. Low installation depth of only 36 mm. LED converter in a separate housing made of plastics with throughwiring terminals and strain relief. Required depth for entering the ceiling only 100mm.

Symmetric white beam light distribution for enlarged spacing with mounting heights of

up to 8.5 m. Maximum spacing between luminaires:

> 10.8 m as from 3 m mounting height up to 15 m at 7 to 8.5 m height

(basis of calculation at least 1 lx in centre of escape route - maintenance factor WF = 0.8)

Light source: 4 x high efficient, white HighPower LEDs 1.1 W with a service life of 50.000 h  on account of optimised LED operating conditions.

Special LED converter with integrated monitoring module for single luminaire monitoring

with twenty addresses for fault and performance monitoring (CEWA GUARD technology).

Freely programmable mixed operation of the connection systems (Maintained light, non maintained light and switched maintained light) within a circuit without additional data or actuating cables to the luminaires is possible in combination with suitable safety lighting system with STAR technology.

Luminous flux at the end of the rated service time:	100%

Housing material: 					aluminium, steel, PC

Housing colour: 					white (similar to RAL 9010)

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		25 mA

Power consumption including LED supply

(apparent power / effective power): 			9.5 VA / 5.8 W.

Class of protection:					II

Type of protection					IP 20

Permissible ambient temperature: 			-20° Celsius to +40° Celsius

Dimensions (mm) :					D = 80 H = 38

Housing for LED converter:

L = (132 + 85), H = 26, T = 47 (bent construction)

Dimensions - ceiling cutout (mm):			Diameter = 68 mm

Type: 3504.1 LED CG-S white

Make: CEAG

SL 3504.1 LED CG-S stainless steel

Pos.    )		ea.

Safety luminaire in LED technology with symmetric light distribution for recessed installation in keeping with German / European standards DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for operation on safety illumination systems in keeping with German / European standards DIN VDE 0100-718, DIN EN 50172 and E DIN VDE 0108-100; developed, manufactured and tested in keeping with ISO 9001.

Round Bezel with 80 mm diameter, made of brushed stainless steel. Installation of the luminaire without use of tools by clamping springs for ceiling thicknesses of up to 20 mm. Drill hole diameter 68 mm. Low installation depth of only 36 mm. LED converter in a separate housing made of plastics with throughwiring terminals and strain relief. Required depth for entering the ceiling only 100mm.

Symmetric white beam light distribution for enlarged spacing with mounting heights of

up to 8.5 m. Maximum spacing between luminaires:

> 10.8 m as from 3 m mounting height up to 15 m at 7 to 8.5 m height

(basis of calculation at least 1 lx in centre of escape route - maintenance factor WF = 0.8)

Light source: 4 x high efficient, white HighPower LEDs 1.1 W with a service life of 50.000 h  on account of optimised LED operating conditions.

Special LED converter with integrated monitoring module for single luminaire monitoring

with twenty addresses for fault and performance monitoring (CEWA GUARD technology).

Freely programmable mixed operation of the connection systems (Maintained light, non maintained light and switched maintained light) within a circuit without additional data or actuating cables to the luminaires is possible in combination with suitable safety lighting system with STAR technology.

Luminous flux at the end of the rated service time:	100%

Housing material: 					aluminium, steel, PC

Housing colour: 					stainless steel brushed

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		25 mA

Power consumption including LED supply

(apparent power / effective power): 			9.5 VA / 5.8 W

Class of protection:					II

Type of protection					IP 20

Permissible ambient temperature: 			-20° Celsius to +40° Celsius

Dimensions (mm) :					D = 80 H = 38

Housing for LED converter:

L = (132 + 85), H = 26, T = 47 (bent construction)

Dimensions - ceiling cutout (mm):			Diameter = 68 mm

Type: 3504.1 LED CG-S stainless steel

Make: CEAG

SL 3604.1 LED CG-S white

Pos.    )		ea.

Safety luminaire in LED technology with symmetric light distribution for recessed installation in keeping with German / European standards DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for operation on safety illumination systems in keeping with German / European standards DIN VDE 0100-718, DIN EN 50172 and E DIN VDE 0108-100; developed, manufactured and tested in keeping with ISO 9001.

Quadratic bezel with 80 mm x 80 mm, laquered white (similar to RAL 9010).  Installation of the luminaire without use of tools by clamping springs for ceiling thicknesses of up to 20 mm. Drill hole diameter 68 mm. Low installation depth of only 36 mm. LED converter in a separate housing made of plastics with throughwiring terminals and strain relief. Required depth for entering the ceiling only 100mm.

Symmetric white beam light distribution for enlarged spacing with mounting heights of

up to 8.5 m. Maximum spacing between luminaires:

> 10.8 m as from 3 m mounting height up to 15 m at 7 to 8.5 m height

(basis of calculation at least 1 lx in centre of escape route - maintenance factor WF = 0.8)

Light source: 4 x high efficient, white HighPower LEDs 1.1 W with a service life of 50.000 h  on account of optimised LED operating conditions.

Special LED converter with integrated monitoring module for single luminaire monitoring

with twenty addresses for fault and performance monitoring (CEWA GUARD technology).

Freely programmable mixed operation of the connection systems (Maintained light, non maintained light and switched maintained light) within a circuit without additional data or actuating cables to the luminaires is possible in combination with suitable safety lighting system with STAR technology.

Luminous flux at the end of the rated service time:	100%

Housing material: 					aluminium, steel, PC

Housing colour: 					white (similar to RAL 9010)

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		25 mA

Power consumption including LED supply

(apparent power / effective power): 			9.5 VA / 5.8 W.

Class of protection:					II

Type of protection					IP 20

Permissible ambient temperature: 			-20° Celsius to +40° Celsius

Dimensions (mm) :					L = 80, W = 80, H = 35

Housing for LED converter:

L = (132 + 85), H = 26, T = 47 (bent construction)

Dimensions - ceiling cutout (mm):			Diameter = 68 mm

Type: 3604.1 LED CG-S white

Make: CEAG

SL 3604.1 LED CG-S stainless steel

Pos.    )		ea.

Safety luminaire in LED technology with symmetric light distribution for recessed installation in keeping with German / European standards DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for operation on safety illumination systems in keeping with German / European standards DIN VDE 0100-718, DIN EN 50172 and E DIN VDE 0108-100; developed, manufactured and tested in keeping with ISO 9001.

Quadratic bezel with 80 mm x 80 mm, made of brushed stainless steel. Installation of the luminaire without use of tools by clamping springs for ceiling thicknesses of up to 20 mm. Drill hole diameter 68 mm. Low installation depth of only 36 mm. LED converter in a separate housing made of plastics with throughwiring terminals and strain relief. Required depth for entering the ceiling only 100mm.

Symmetric white beam light distribution for enlarged spacing with mounting heights of

up to 8.5 m. Maximum spacing between luminaires:

> 10.8 m as from 3 m mounting height up to 15 m at 7 to 8.5 m height

(basis of calculation at least 1 lx in centre of escape route - maintenance factor WF = 0.8)

Light source: 4 x high efficient, white HighPower LEDs 1.1 W with a service life of 50.000 h on account of optimised LED operating conditions.

Special LED converter with integrated monitoring module for single luminaire monitoring

with twenty addresses for fault and performance monitoring (CEWA GUARD technology).

Freely programmable mixed operation of the connection systems (Maintained light, non maintained light and switched maintained light) within a circuit without additional data or actuating cables to the luminaires is possible in combination with suitable safety lighting system with STAR technology.

Luminous flux at the end of the rated service time:	100%

Housing material: 					aluminium, steel, PC

Housing colour: 					stainless steel brushed

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		25 mA

Power consumption including LED supply

(apparent power / effective power): 			9.5 VA / 5.8 W

Class of protection:					II

Type of protection					IP 20

Permissible ambient temperature: 			-20° Celsius to +40° Celsius

Dimensions (mm) :					L = 80, W = 80, H = 35

Housing for LED converter:

L = (132 + 85), H = 26, T = 47 (bent construction)

Dimensions - ceiling cutout (mm):			Diameter = 68 mm

Type: 3604.1 LED CG-S stainless steel

Make: CEAG