GuideLed 10011 CG-S - for wall surface mounting

Pos.    )		ea.

One-sided LED exit sign luminaire in keeping with German / European standards EN 60598-1, DIN EN 60598-2-22, DIN 4844-1 and DIN EN 1838 with surface mounting set; developed, manufactured and tested in keeping with ISO 9001.

Exit sign in LED lightguide technology for especially uniform and

bright illuminationof the pictogram:

Lm >= 500 cd/m²  of the white contrasting colour and

Lm >= 200 cd/m² across the entire pictogram

Uniformity Lmin/Lmax > 0.8.

High service life ensured by optimised LED operating conditions.

Increased safety ensured by redundant construction of the LED unit consisting of three-chip LEDs with high light efficiency > 100 lm/W for distinctly reduced connected load.

Power consumption including LED supply (apparent power / effective power): 4.0 VA / 1.9 W.

Reverse polarity protected wiring of the LED unit.

Slender design with low mounting height of only 36 mm including pictogram and mounting set.

Installation of the LED pictogram without tools on the surface mounting set.

Special LED converter with integrated monitoring module for single luminaire monitoring

with 20-digit address switches.

Mixed operation of the connection systems (maintained light, non-maintained light and switched maintained light within a circuit without additional data or actuating cables to the luminaires is possible in combination with suitable group or central battery systems with STAR technology.

Viewing distance:					20 m

Luminous flux at the end of the rated service time:	100%

Housing material: 					PC, PMMA

Housing colour: 					light grey RAL 7035

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		8 mA

Class of protection:					II

Type of protection					IP 41

Permissible ambient temperature: 			-20° Celsius to +40° Celsius

Dimensions - LED pictogram (mm):			W = 226, H = 134,  D = 13

Dimensions including wall mounting set:  		W = 226, H = 134,  D = 36

Accessories:

..... ..... ea.  feed-through wiring for GuideLed 10011 CG-S

Type: GuideLed 10011 CG-S - for wall surface mounting

Make: CEAG

GuideLed  10012 CG-S – for semi-recessed installation

Pos.    )		ea.

One-sided LED exit sign luminaire in keeping with German / European standards EN 60598-1, DIN EN 60598-2-22, DIN 4844-1 and DIN EN 1838 with semi-recessed mounting set for installation of the LED converter e.g. in a double-device socket in keeping with German standard DIN 49073; developed, manufactured and tested in keeping with ISO 9001.

Exit sign in LED lightguide technology for especially uniform and

bright illuminationof the pictogram:

Lm >= 500 cd/m²  of the white contrasting colour and

Lm >= 200 cd/m² across the entire pictogram

Uniformity Lmin/Lmax > 0.8.

High service life ensured by optimised LED operating conditions.

Increased safety ensured by redundant construction of the LED unit consisting of three-chip LEDs with high light efficiency > 100 lm/W for distinctly reduced connected load.

Power consumption including LED supply (apparent power / effective power): 4.0 VA / 1.9 W.

Reverse polarity protected wiring of the LED unit.

Slender design with low mounting height of only 14 mm including pictogram and mounting set.

Installation of the LED pictogram without tools on the mounting set.

Special LED converter with integrated monitoring module for single luminaire monitoring

with 20-digit address switches.

Mixed operation of the connection systems (maintained light, non-maintained light and switched maintained light within a circuit without additional data or actuating cables to the luminaires is possible in combination with suitable group or central battery systems with STAR technology.

Viewing distance:					20 m

Luminous flux at the end of the rated service time:	100%

Housing material: 					PC, PMMA

Housing colour: 					light grey RAL 7035

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		8 mA

Class of protection:					II

Type of protection					IP 41

Permissible ambient temperature: 			-20° Celsius to +40° Celsius

Dimensions - LED pictogram (mm):			W = 226, H = 134,  D = 13

Dimensions including wall mounting set:  		W = 226, H = 134,  D = 14

Type: GuideLed  10012 CG-S – for semi-recessed installation

Make: CEAG

GuideLed 10011 CG-S - for wall surface mounting

Pos.    )		ea.

One-sided LED exit sign luminaire in keeping with German / European standards EN 60598-1, DIN EN 60598-2-22, DIN 4844-1 and DIN EN 1838 with surface mounting set; developed, manufactured and tested in keeping with ISO 9001.

Exit sign in LED lightguide technology for especially uniform and

bright illuminationof the pictogram:

Lm >= 500 cd/m²  of the white contrasting colour and

Lm >= 200 cd/m² across the entire pictogram

Uniformity Lmin/Lmax > 0.8.

High service life ensured by optimised LED operating conditions.

Increased safety ensured by redundant construction of the LED unit consisting of three-chip LEDs with high light efficiency > 100 lm/W for distinctly reduced connected load.

Power consumption including LED supply (apparent power / effective power): 5.0 VA / 2.6 W.

Reverse polarity protected wiring of the LED unit.

Slender design with low mounting height of only 36 mm including pictogram and mounting set.

Installation of the LED pictogram without tools on the surface mounting set.

Special LED converter with integrated monitoring module for single luminaire monitoring

with 20-digit address switches.

Mixed operation of the connection systems (maintained light, non-maintained light and switched maintained light within a circuit without additional data or actuating cables to the luminaires is possible in combination with suitable group or central battery systems with STAR technology.

Viewing distance:					30 m

Luminous flux at the end of the rated service time:	100%

Housing material: 					PC, PMMA

Housing colour: 					light grey RAL 7035

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		11 mA

Class of protection:					II

Type of protection					IP 41

Permissible ambient temperature: 			-20° Celsius to +40° Celsius

Dimensions - LED pictogram (mm):			W = 327, H = 184,  D = 13

Dimensions including wall mounting set:  		W = 327, H = 184,  D = 36

Accessories:

..... ..... ea.  feed-through wiring for GuideLed 11011 CG-S

Type: GuideLed 10011 CG-S - for wall surface mounting

Make: CEAG

GuideLed  11012 CG-S – for semi-recessed installation

Pos.    )		ea.

One-sided LED exit sign luminaire in keeping with German / European standards EN 60598-1, DIN EN 60598-2-22, DIN 4844-1 and DIN EN 1838 with semi-recessed mounting set for installation of the LED converter e.g. in a double-device socket in keeping with German standard DIN 49073; developed, manufactured and tested in keeping with ISO 9001.

Exit sign in LED lightguide technology for especially uniform and

bright illuminationof the pictogram:

Lm >= 500 cd/m²  of the white contrasting colour and

Lm >= 200 cd/m² across the entire pictogram

Uniformity Lmin/Lmax > 0.8.

High service life ensured by optimised LED operating conditions.

Increased safety ensured by redundant construction of the LED unit consisting of three-chip LEDs with high light efficiency > 100 lm/W for distinctly reduced connected load.

Power consumption including LED supply (apparent power / effective power): 5.0 VA / 2.6 W.

Reverse polarity protected wiring of the LED unit.

Slender design with low mounting height of only 14 mm including pictogram and mounting set.

Installation of the LED pictogram without tools on the mounting set.

Special LED converter with integrated monitoring module for single luminaire monitoring

with 20-digit address switches.

Mixed operation of the connection systems (maintained light, non-maintained light and switched maintained light within a circuit without additional data or actuating cables to the luminaires is possible in combination with suitable group or central battery systems with STAR technology.

Viewing distance:					30 m

Luminous flux at the end of the rated service time:	100%

Housing material: 					PC, PMMA

Housing colour: 					light grey RAL 7035

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		11 mA

Class of protection:					II

Type of protection					IP 41

Permissible ambient temperature: 			-20° Celsius to +40° Celsius

Dimensions - LED pictogram (mm):			W = 327, H = 184,  D = 13

Dimensions including wall mounting set:  		W = 327, H = 184,  D = 14

Type: GuideLed  11012 CG-S – for semi-recessed installation

Make: CEAG