GuideLed SL 13011 CG-S recessed mounted ceiling luminaire with symmetric light distribution

Pos.    )		ea.

Safety luminaire in LED technology with symmetric light distribution for recessed installation in keeping with German / European standards DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for operation on safety illumination systems in keeping with German / European standards DIN VDE 0100-718, DIN EN 50172 and E DIN VDE 0108-100; developed, manufactured and tested in keeping with ISO 9001.

Symmetric light distribution for uniform anti-panic or open space illumination with mounting heights of

up to 6.5 m. Maximum spacing between luminaires:

> 9 m as from 3 m mounting height

11.4 m at 5 m height  (basis for calculation: room illumination with at least 1lx; maintenance factor = 0.8)

Light direction by means double optics technology combined with reflection-enhanced reflectors integrated in the luminaires. Light source: 2 x highly efficient, white high-power LEDs 2 W,  with a service life of 50,000 h on account of optimised LED operating conditions.

Rectangular design with almost flush ceiling appearance: visible housing parts only 1.5 mm high consisting of a frame (polycarbonate) and clear top cover (PMMA). Low installation depth of only 36 mm. Heat sink made of aluminium die cast. Installation of the luminaire without the use of tools by clamping springs for ceiling thicknesses of up to 20 mm. LED converter in separate plastic housing with feed-through wiring terminal 2.5 mm² and strain relief for primary and secondary connection.

Special LED converter with integrated monitoring module for single luminaire monitoring

with twenty addresses for fault and performance monitoring (CEWA GUARD technology).

Freely programmable mixed operation of the connection systems (Maintained light, non maintained light and switched maintained light) within a circuit without additional data or actuating cables to the luminaires is possible in combination with suitable safety lighting system with STAR technology.

Power consumption including LED supply (apparent power / effective power): 8.5 VA / 5.0 W.

Luminous flux at the end of the rated service time:	100%

Housing material: 					aluminium die cast, PC, PMMA

Housing colour: 					white RAL 9010

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		21.5 mA

Class of protection:					I

Type of protection					IP 40

Permissible ambient temperature: 			-20° Celsius to +40° Celsius

Dimensions (mm) :					L = 97, W = 97,  H = 38

Housing for LED converter:

L = 290, W = 50,  H = 33

Dimensions - ceiling cutout (mm):			L = 87, W = 87

Type: GuideLed  SL  13011 CG-S – recessed installation with symmetric light distribution

Make: CEAG

GuideLed SL 13021 CG-S recessed mounted ceiling luminaire with asymmetric light distribution

Pos.    )		ea.

Safety luminaire in LED technology with asymmetric light distribution for recessed installation in keeping with German / European standards DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for operation on safety illumination systems in keeping with German / European standards DIN VDE 0100-718, DIN EN 50172 and E DIN VDE 0108-100; developed, manufactured and tested in keeping with ISO 9001.

Asymmetric light distribution for especially efficient escape route illumination with at least 1 lx

in keeping with German / European standard DIN EN 1838 for mounting heights of up to 8.5 m. Maximum spacing between luminaires:

> 15 m as from 3 m mounting height

> 20 m as from 5 m mounting height (basis of calculation at least 1 lx in centre of escape route - maintenance factor = 0.8)

Light direction by means double optics technology combined with reflection-enhanced reflectors integrated in the luminaires. Light source: 2 x highly efficient, white high-power LEDs 2 W,  with a service life of 50,000 h on account of optimised LED operating conditions.

Rectangular design with almost flush ceiling appearance: visible housing parts only 1.5 mm high consisting of a frame (polycarbonate) and clear top cover (PMMA). Low installation depth of only 36 mm. Heat sink made of aluminium die cast. Installation of the luminaire without the use of tools by clamping springs for ceiling thicknesses of up to 20 mm. LED converter in separate plastic housing with feed-through wiring terminal 2.5 mm² and strain relief for primary and secondary connection.

Special LED converter with integrated monitoring module for single luminaire monitoring

with twenty addresses for fault and performance monitoring (CEWA GUARD technology).

Freely programmable mixed operation of the connection systems (Maintained light, non maintained light and switched maintained light) within a circuit without additional data or actuating cables to the luminaires is possible in combination with suitable safety lighting system with STAR technology.

Power consumption including LED supply (apparent power / effective power): 8.5 VA / 5.0 W.

Luminous flux at the end of the rated service time:	100%

Housing material: 					aluminium die cast, PC, PMMA

Housing colour: 					white RAL 9010

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		21.5 mA

Class of protection:					I

Type of protection					IP 40

Permissible ambient temperature: 			-20° Celsius to +40° Celsius

Dimensions (mm) :					L = 97, W = 97,  H = 38

Housing for LED converter:

L = 290, W = 50,  H = 33

Dimensions - ceiling cutout (mm):			L = 87, W = 87

Type: GuideLed SL 13021 CG-S - recessed installation with asymmetric light distribution

Make: CEAG

GuideLed SL 13012 CG-S surface mounted ceiling luminaire with symmetric light distribution

Pos.    )		ea.

Safety luminaire in LED technology with symmetric light distribution for ceiling installation in keeping with German / European standards DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for operation on safety illumination systems in keeping with German / European standards DIN VDE 0100-718, DIN EN 50172 and E DIN VDE 0108-100; developed, manufactured and tested in keeping with ISO 9001.

Symmetric light distribution for uniform anti-panic or open space illumination with mounting heights of up to 6.5 m. Maximum spacing between luminaires:

> 9 m as from 3 m mounting height

11.4 m at 5 m height  (basis for calculation: room illumination with at least 1lx maintenance factor = 0.8)

Light direction by means double optics technology combined with reflection-enhancing reflectors integrated in the luminaires. Light source: 2 x highly efficient, white high-power LEDs 2 W,  with a service life of 50,000 h on account of optimised LED operating conditions.

Housing close to the ceiling made of aluminium die cast for optimised heat distribution. Visible housing made of white polycarbonate (RAL 9010) and transparent pane (PMMA). Cable entry from above or from one side optionally.

Special LED converter with integrated monitoring module for single luminaire monitoring

with twenty addresses for fault and performance monitoring (CEWA GUARD technology).

Freely programmable mixed operation of the connection systems (Maintained light, non maintained light and switched maintained light) within a circuit without additional data or actuating cables to the luminaires is possible in combination with suitable safety lighting system with STAR technology.

Power consumption including LED supply (apparent power / effective power): 8.5 VA / 5.0 W.

Luminous flux at the end of the rated service time:	100%

Housing material: 					aluminium die cast, PC, PMMA

Housing colour: 					white RAL 9010

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		21.5 mA

Class of protection:					I

Type of protection					IP 40

Permissible ambient temperature: 			-20° Celsius to +40° Celsius

Dimensions (mm) :					L = 140, W = 140,  H = 30

Type: GuideLed  SL  13012 CG-S – surface installation with symmetric light distribution

Make: CEAG

GuideLed SL 13022 CG-S surface mounted ceiling luminaire with asymmetric light distribution

Pos.    )		ea.

Safety luminaire in LED technology with asymmetric light distribution for surface installation in keeping with German / European standards DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for operation on safety illumination systems in keeping with German / European standards DIN VDE 0100-718, DIN EN 50172 and E DIN VDE 0108-100; developed, manufactured and tested in keeping with ISO 9001.

Asymmetric light distribution for especially efficient escape route illumination with at least 1 lx

in keeping with German / European standard DIN EN 1838 for mounting heights of up to 8.5 m. Maximum spacing between luminaires:

> 15 m as from 3 m mounting height

> 20 m as from 5 m mounting height (basis of calculation at least 1 lx in centre of escape route - maintenance factor WF = 0.8)

Light direction by means double optics technology combined with reflection-enhanced reflectors integrated in the luminaires. Light source: 2 x highly efficient, white high-power LEDs 2 W,  with a service life of 50,000 h on account of optimised LED operating conditions.

Housing close to the ceiling made of aluminium die cast for optimised heat distribution. Visible housing made of white polycarbonate (RAL 9010) and transparent pane (PMMA). Cable entry from above or from one side optionally.

Special LED converter with integrated monitoring module for single luminaire monitoring

with twenty addresses for fault and performance monitoring (CEWA GUARD technology).

Freely programmable mixed operation of the connection systems (Maintained light, non maintained light and switched maintained light) within a circuit without additional data or actuating cables to the luminaires is possible in combination with suitable safety lighting system with STAR technology.

Power consumption including LED supply (apparent power / effective power): 8.5 VA / 5.0 W.

Luminous flux at the end of the rated service time:	100%

Housing material: 					aluminium die cast, PC, PMMA

Housing colour: 					white RAL 9010

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		21.5 mA

Class of protection:					I

Type of protection					IP 40

Permissible ambient temperature: 			-20° Celsius to +40° Celsius

Dimensions (mm) :					L = 140, W = 140,  H = 30

Type: GuideLed SL 13022 CG-S surface installation with asymmetric light distribution

Make: CEAG