GuideLed  10025 CG-S – for rope ceiling installation

Pos.    )		ea.

Double-sided LED exit sign luminaire in keeping with German / European standards EN 60598-1, DIN EN 60598-2-22, DIN 4844-1 and DIN EN 1838 with 0.5 m rope mounting set including transparent insulated rope suspension for power supply and canopy used to house the LED converter; developed, manufactured and tested in keeping with ISO 9001.

Exit sign in LED lightguide technology for especially uniform and

bright illuminationof the pictogram:

Lm >= 500 cd/m²  of the white contrasting colour and

Lm >= 200 cd/m² across the entire pictogram

Uniformity Lmin/Lmax > 0.8.

High service life ensured by optimised LED operating conditions.

Increased safety ensured by redundant construction of the LED unit consisting of three-chip LEDs with high light efficiency > 100 lm/W for distinctly reduced connected load.

Power consumption including LED supply (apparent power / effective power):

5.5 VA / 2.9 W  	(4.0 VA / 1.9 W for PL/BL, PR/BL and PU/BL variants)

Reverse polarity protected wiring of the LED unit.

Slender design with narrow pictogram width of only 12 mm and a canopy of only 29 mm in height. Freely adjustable suspension height by means of wire rope holders up to 1.0 m - no tools required.

Special LED converter with integrated monitoring module for single luminaire monitoring with 20-digit address switches.

Mixed operation of the connection systems (maintained light, non-maintained light and switched maintained light within a circuit without additional data or actuating cables to the luminaires is possible in combination with suitable group or central battery systems with STAR technology.

Viewing distance:					20 m

Luminous flux at the end of the rated service time:	100%

Housing material: 					PC, PMMA

Housing colour: 					light grey RAL 7035

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		12 mA

(8 mA for PL/BL, PR/BL and PU/BL variants)

Class of protection:					II

Type of protection					IP 41

Permissible ambient temperature: 			-20° Celsius to +40° Celsius

Dimensions - LED pictogram (mm):			W = 226, H = 134,  D = 12

Dimensions - canopy	:  				W = 226, H = 29,  D = 42

Type: GuideLed  10025 CG-S – for rope ceiling installation

Make: CEAG

GuideLed  10026 CG-S – for ceiling installation with rope suspension

Pos.    )		ea.

Double-sided LED exit sign luminaire in keeping with German / European standards EN 60598-1, DIN EN 60598-2-22, DIN 4844-1 and DIN EN 1838 with rope installation set. Including transparent insulated rope suspension for power supply, chromium-plated ceiling feed-through and plastic housing to be placed in ceiling for the LED converter with strain relief on the primary and secondary side; developed, manufactured and tested in keeping with ISO 9001.

Exit sign in LED lightguide technology for especially uniform and

bright illuminationof the pictogram:

Lm >= 500 cd/m²  of the white contrasting colour and

Lm >= 200 cd/m² across the entire pictogram

Uniformity Lmin/Lmax > 0.8.

High service life ensured by optimised LED operating conditions.

Increased safety ensured by redundant construction of the LED unit consisting of three-chip LEDs with high light efficiency > 100 lm/W for distinctly reduced connected load.

Power consumption including LED supply (apparent power / effective power):

5.5 VA / 2.9 W  	(4.0 VA / 1.9 W for PL/BL, PR/BL and PU/BL variants)

Reverse polarity protected wiring of the LED unit.

Slender design with narrow pictogram width of only 12 mm and a canopy of only 29 mm in height. Continuously adjustable suspension height up to 1.0 m.

Special LED converter with integrated monitoring module for single luminaire monitoring with 20-digit address switches.

Mixed operation of the connection systems (maintained light, non-maintained light and switched maintained light within a circuit without additional data or actuating cables to the luminaires is possible in combination with suitable group or central battery systems with STAR technology.

Viewing distance:					20 m

Luminous flux at the end of the rated service time:	100%

Housing material: 					PC, PMMA

Housing colour: 					light grey RAL 7035

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		12 mA

(8 mA for PL/BL, PR/BL and PU/BL variants)

Class of protection:					II

Type of protection					IP 41

Permissible ambient temperature: 			-20° Celsius to +40° Celsius

Dimensions - LED pictogram (mm):			W = 226, H = 134,  D = 12

Dimensions - canopy	:  				W = 226, H = 29,  D = 42

Type: GuideLed  10026 CG-S – for ceiling installation with rope suspension

Make: CEAG

GuideLed  11025 CG-S – for rope ceiling installation

Pos.    )		ea.

Double-sided LED exit sign luminaire in keeping with German / European standards EN 60598-1, DIN EN 60598-2-22, DIN 4844-1 and DIN EN 1838 with 0.5 m rope mounting set including transparent insulated rope suspension for power supply and canopy used to house the LED converter; developed, manufactured and tested in keeping with ISO 9001.

Exit sign in LED lightguide technology for especially uniform and

bright illuminationof the pictogram:

Lm >= 500 cd/m²  of the white contrasting colour and

Lm >= 200 cd/m² across the entire pictogram

Uniformity Lmin/Lmax > 0.8.

High service life ensured by optimised LED operating conditions.

Increased safety ensured by redundant construction of the LED unit consisting of three-chip LEDs with high light efficiency > 100 lm/W for distinctly reduced connected load.

Power consumption including LED supply (apparent power / effective power):

7.1 VA / 4.1 W  	(5.0 VA / 2.6 W for PL/BL, PR/BL and PU/BL variants)

Reverse polarity protected wiring of the LED unit.

Slender design with narrow pictogram width of only 12 mm and a canopy of only 29 mm in height. Freely adjustable suspension height by means of wire rope holders up to 1.0 m - no tools required.

Special LED converter with integrated monitoring module for single luminaire monitoring with 20-digit address switches.

Mixed operation of the connection systems (maintained light, non-maintained light and switched maintained light within a circuit without additional data or actuating cables to the luminaires is possible in combination with suitable group or central battery systems with STAR technology.

Viewing distance:					30 m

Luminous flux at the end of the rated service time:	100%

Housing material: 					PC, PMMA

Housing colour: 					light grey RAL 7035

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		17 mA

(11 mA for PL/BL, PR/BL and PU/BL variants)

Class of protection:					II

Type of protection					IP 41

Permissible ambient temperature: 			-20° Celsius to +40° Celsius

Dimensions - LED pictogram (mm):			W = 327, H = 184,  D = 12

Dimensions - canopy	:  				W = 327, H = 29,  D = 42

Type: GuideLed  11025 CG-S – for rope ceiling installation

Make: CEAG

GuideLed  11026 CG-S – for ceiling installation with rope suspension

Pos.    )		ea.

Double-sided LED exit sign luminaire in keeping with German / European standards EN 60598-1, DIN EN 60598-2-22, DIN 4844-1 and DIN EN 1838 with rope installation set. Including transparent insulated rope suspension for power supply, chromium-plated ceiling feed-through and plastic housing to be placed in ceiling for the LED converter with strain relief on the primary and secondary side; developed, manufactured and tested in keeping with ISO 9001.

Exit sign in LED lightguide technology for especially uniform and

bright illuminationof the pictogram:

Lm >= 500 cd/m²  of the white contrasting colour and

Lm >= 200 cd/m² across the entire pictogram

Uniformity Lmin/Lmax > 0.8.

High service life ensured by optimised LED operating conditions.

Increased safety ensured by redundant construction of the LED unit consisting of three-chip LEDs with high light efficiency > 100 lm/W for distinctly reduced connected load.

Power consumption including LED supply (apparent power / effective power):

7.1 VA / 4.1 W  	(5.0 VA / 2.6 W for PL/BL, PR/BL and PU/BL variants)

Reverse polarity protected wiring of the LED unit.

Slender design with narrow pictogram width of only 12 mm and a canopy of only 29 mm in height. Continuously adjustable suspension height up to 1.0 m.

Special LED converter with integrated monitoring module for single luminaire monitoring with 20-digit address switches.

Mixed operation of the connection systems (maintained light, non-maintained light and switched maintained light within a circuit without additional data or actuating cables to the luminaires is possible in combination with suitable group or central battery systems with STAR technology.

Viewing distance:					30 m

Luminous flux at the end of the rated service time:	100%

Housing material: 					PC, PMMA

Housing colour: 					light grey RAL 7035

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		17 mA

(11 mA for PL/BL, PR/BL and PU/BL variants)

Class of protection:					II

Type of protection					IP 41

Permissible ambient temperature: 			-20° Celsius to +40° Celsius

Dimensions - LED pictogram (mm):			W = 327, H = 184,  D = 12

Dimensions - canopy	:  				W = 327, H = 29,  D = 42

Type: GuideLed  11026 CG-S – for ceiling installation with rope suspension

Make: CEAG