# SL 72011 CG-S

Pos. ...)  ... pcs.

Emergency Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Enclosure made of slim aluminium profile, tarnished anodized with clear cover. Additional light outlet bottom side.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cutoff for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Max. spacing between luminaire/luminaire and clear cover = 11,4 m

(mounting height = 7 m, C0 level, Emin = 1.25 lx, (luminous flux at the end of the rated duration)

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 30 mA

Power consumption: 16 VA

Permissible temperature range: -10°C up to +40°C

Loop terminals: 3 x 2.5 sqmm

Insulation class: I; Degree of protection: IP 40

Colour of enclosure: Aluminium anodized

Inclusive lamp: 8 W T16, 450 Im

Dimensions (mm): L = 431, H = 230, D = 80

Type: SL 72011 CG-S

Manufactured by: CEAG

Pos. ...)  ... pcs.

# RZ  72011 CG-S

Pos. ...)  ... pcs.

Exit Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Enclosure made of slim aluminium profile, tarnished anodized with clear cover. Additional light outlet bottom side.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cutoff for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Marking: single-sided silk screened legend

Viewing distance: 40 m

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 30 mA

Power consumption: 16 VA

Permissible temperature range: -10°C up to +40°C

Loop terminals: 3 x 2.5 sqmm

Insulation class: II; Degree of protection: IP 40

Colour of enclosure: Aluminium anodized

Inclusive lamp: 8 W T16, 450 Im

Dimensions (mm): L = 431, H = 230, D = 80

Type: RZ 72011 CG-S

Manufactured by: CEAG

RZ  72021 WM CG-S

Pos. ...)  ... pcs.

Exit Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Enclosure made of slim aluminium profile, tarnished anodized with clear cover. Additional light outlet bottom side.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cutoff for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Mounting: Wall Mounting 90°

Marking: double-sided silk screened legend

Viewing distance: 40 m

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 30 mA

Power consumption: 16 VA

Permissible temperature range: -10°C up to +40°C

Loop terminals: 3 x 2.5 sqmm

Insulation class: I; Degree of protection: IP 40

Colour of enclosure: Aluminium anodized

Inclusive lamp: 8 W T16, 450 Im

Dimensions (mm): L = 431, H = 230, D = 80

Type: RZ 72021 WM CG-S

Manufactured by: CEAG

Pos. ...)  ... pcs.

Accessories:

- clear cover, structured

- dummy cover

Manufactured by: CEAG

# RZ  72021 DM CG-S

Pos. ...)  ... pcs.

Exit Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Enclosure made of slim aluminium profile, tarnished anodized with clear cover. Additional light outlet bottom side.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cutoff for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Mounting: Direct ceiling Mounting

Marking: double-sided silk screened legend

Viewing distance: 40 m

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 30 mA

Power consumption: 16 VA

Permissible temperature range: -10°C up to +40°C

Loop terminals: 3 x 2.5 sqmm

Insulation class: I; Degree of protection: IP 40

Colour of enclosure: Aluminium anodized

Inclusive lamp: 8 W T16, 450 Im

Dimensions (mm): L = 431, H = 230, D = 80

Type: RZ 72021 DM CG-S

Manufactured by: CEAG

Pos. ...)  ... pcs.

Accessories:

- clear cover, structured

- dummy cover

Manufactured by: CEAG

# RZ  72021 PM CG-S

Pos. ...)  ... pcs.

Exit Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Enclosure made of slim aluminium profile, tarnished anodized with clear cover. Additional light outlet bottom side.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cutoff for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Mounting: Pendulum Mounting

Marking: double-sided silk screened legend

Viewing distance: 40 m

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 30 mA

Power consumption: 16 VA

Permissible temperature range: -10°C up to +40°C

Loop terminals: 3 x 2.5 sqmm

Insulation class: I; Degree of protection: IP 40

Colour of enclosure: Aluminium anodized

Inclusive lamp: 8 W T16, 450 Im

Dimensions (mm): L = 431, H = 231, D = 80

Type: RZ 72021 PM CG-S

Manufactured by: CEAG

Pos. ...)  ... pcs.

Accessories:

- Pendulum set 0,5 m with canopy , silver

- Pendulum set 1,0 m with canopy , silver

- Pendulum set 1,5 m with canopy , silver

- chain suspension

- clear cover, structured

- dummy cover

Manufactured by: CEAG