# 40011 CG-S

Pos. ...)  ... pcs.

Emergency Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Modular designed luminaire with robust die-cast aluminium enclosure, automatic cutout for failures within the lamp circuit, clear cover made of 850°C glow wire resistant, halogen-free polycarbonate for tool-free assembly.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Max. spacing between luminaire/luminaire and clear cover= 17.8 m

(mounting height = 5 m, C0 level, Emin = 1.25 lx, (luminous flux at the end of the rated duration)

Voltage range: 230 V 50/60 Hz, 220 V DC +25/-20 %

Current drawn (battery operation): 30 mA

Power consumption: 16 VA

Permissible temperature range: -10 °C up to +40 °C

Loop terminals: 3 x 2.5 sqmm

Insulation class I; Degree of protection IP 41

Colour of enclosure: RAL 7035

Inclusive lamp: 8 W T16, 450 Im

Dimensions (mm): L = 345, H = 200, D = 80

Type: SL 40011 CG-S

Manufactured by: CEAG

Pos. ...)  ... pcs.

Accessories:

- Wire guard

- IP 54 set, marked

- 2 x M20 cable glands

Manufactured by: CEAG

# 40011 CG-S

Pos. ...)  ... pcs.

Exit Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Modular designed luminaire with robust die-cast aluminium enclosure, automatic cutout for failures within the lamp circuit, clear cover made of 850°C glow wire resistant, halogen-free polycarbonate for tool-free assembly.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Marking: single-sided silk screened legend

Viewing distance: 32 m

Voltage range: 230 V 50/60 Hz, 220 V DC +25/-20 %

Current drawn (battery operation): 30 mA

Power consumption: 16 VA

Permissible temperature range: -10 °C up to +40 °C

Loop terminals: 3 x 2.5 sqmm

Insulation class I; Degree of protection IP 41

Colour of enclosure: RAL 7035

Inclusive lamp: 8 W T16, 450 Im

Dimensions (mm): L = 345, H = 200, D = 80

Type: RZ 40011 CG-S

Manufactured by: CEAG

Pos. ...)  ... pcs.

Accessories:

- Wire guard

- IP 54 set, marked

- 2 x M20 cable glands

Manufactured by: CEAG