CG-Controller CGLine 400

Pos.   )		Pcs.

CG-Controller CGLine 400 for self-monitoring self-contained luminaires in installations according to EN 50172, DIN VDE 010-718 and E DIN VDE 0108-100.

Microcomputer controlled controller for the central control and monitoring of max. 400 CGLine self-contained luminaires. All of the data and commands are transmitted via 2-core bus cables.

Plastic housing with inspection door, cable ducting from below or the back.

Functions:

- automatic luminaire search function (no manual addressing needed)

- automatic function test, testing distance can be freely selected

- automatic operating duration test, testing distance can be freely selected

- split battery duration test: DT of even / uneven addresses are shifted for 24h

- cancel operating duration test

- block the emergency lighting function (complete or by bus line)

- constant charge monitoring

- communication monitoring

- recording the single fault messages

- status display per luminaire

- free entry of luminaire target destination names, each with 20 characters and abbreviated address assignment via keyboard or by user-friendly PC software

- display output in plain text (display with background lighting), including details of identification number, abbreviated address, individual luminaire names and type of fault per luminaire

– Alphanumeric keypad for programming and entering text on the controller

- freely programmable potential-free alarm contact for battery operation, function test, operating duration test, communication fault, luminaire fault or charging fault.

- LED displays: operation, test and fault

- password protection

- removable configuration and test book memory via memory card for a period of at least 2 years

- evaluation of the test book on memory card using optional card reader and CEAG software on a  
   standard PC

– pre-programming of the configuration memory on the PC

with universal holder for mounting rail systems or wall mounting

Dimensions (mm): H=184mm, W=240. D=112

Connection terminals: 2.5 sq mm

Supply voltage: 230V AC or 24V DC

Safety class II, Degree of protection: IP65

Colour: RAL 7035

Display field: illuminated display, alphanumeric 4 x 20 characters

Keypad: membrane keypad 4 x 4

Alarm contact: 1 x UM, 24 V 0.5A; freely programmable

LED displays: operation, test, fault

Connection terminals for 4 bus lines à 100 CGLine luminaires

Options:

... pcs. SD-card formatted for CG Controller CGLine 400

... pcs. card-reader for memory card

... pcs. CEAG PC Software CGLine 400 for configuration and test book evaluation

Type: CG-Controller CGLine 400

Manufactured by: CEAG