58011- ... D CGLine (SET)

Pos.    )		Pcs.

Self-monitoring self-contained luminaire pursuant to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems pursuant to DIN VDE 0108 / 10.89 for separate operation or for connection to the central monitoring device CG-Controller CGLine 400.

If connected to the central monitoring device CG-Controller CGLine 400 a non-screened 2-core bus cable to the luminaire is also needed.

Standard version with:

- Test button

- Test results with fault analysis (lamps, charging and battery circuit) as well as status displays (operation, function test, duration test) via 3 coloured LEDs

- automatic function test (weekly)

- automatic duration test (every 3 months)

- automatic charging monitoring

- deep discharge protection with restart inhibit

- no-load and short-circuit shut down of the inverter

- block function via CG-Controller CGLine 400

Luminous flux (E/(N approx. 40 %

Lamp: incl. fluorescent tube 8 W, T16/450 Im

Emergency lighting rated operating time:

..... 1 h NC rechargeable battery 3.6 V/1.5 Ah

..... 3 h NC rechargeable battery 3.6 V/4.0 Ah

Permitted temperature range:

Maintained light: -5°C to + 30°C

Non-maintained light: 0°C to +35°C

Housing:

Luminaire with three-sided light emission surface, made of: body of luminaire with EVG (automatic cut-off for failures within the lamp circuit), clear cover with three self-adhesive legend foils. Luminaire enclosure made of 850°C glow wire resistant, halogen-free polycarbonate.

Insulation class: II; Degree of protection: IP 41

Connection terminals: 2.5 sq mm

Supply voltage: 230V 50Hz

Dimensions (mm): L = 342. W = 95. H = 72

Housing colour: light grey / RAL 7035

Viewing distance: 17 m

Luminaires are generally suitable for maintained or non-maintained mode.

Accessories:

..... pcs. IP 54 Set

Type: 58011- ... D CGLine (SET)

Manufactured by: CEAG

58021- ... D CGLine (SET)

Pos.    )		Pcs.

Self-monitoring self-contained luminaire pursuant to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems pursuant to DIN VDE 0108 / 10.89 for separate operation or for connection to the central monitoring device CG-Controller CGLine 400.

If connected to the central monitoring device CG-Controller CGLine 400 a non-screened 2-core bus cable to the luminaire is also needed.

Standard version with:

- Test button

- Test results with fault analysis (lamps, charging and battery circuit) as well as status displays (operation, function test, duration test) via 3 coloured LEDs

- automatic function test (weekly)

- automatic duration test (every 3 months)

- automatic charging monitoring

- deep discharge protection with restart inhibit

- no-load and short-circuit shut down of the inverter

- block function via CG-Controller CGLine 400

Luminous flux (E/(N approx. 40 %

Lamp: incl. fluorescent tube 8 W, T16/450 Im

Emergency lighting rated operating time:

..... 1 h NC rechargeable battery 3.6 V/1.5 Ah

..... 3 h NC rechargeable battery 3.6 V/4.0 Ah

Permitted temperature range:

Maintained light: -5°C to +30°C

Non-maintained light: 0°C to +35°C

Housing:

Luminaire with three-sided light emission surface, made of: body of luminaire with EVG (automatic cut-off for failures within the lamp circuit), clear high cover with four self-adhesive legend foils. Luminaire enclosure made of 850°C glow wire resistant, halogen-free polycarbonate.

Insulation class: II; Degree of protection: IP 41

Connection terminals: 2.5 sq mm

Supply voltage: 230V 50Hz

Dimensions (mm): L = 342. W = 92. D = 137

Housing colour: light grey / RAL 7035

Viewing distance: 17 m

Luminaires are generally suitable for maintained or non-maintained mode.

Accessories:

..... pcs. ceiling-/chain fixing

..... pcs. wall bracket

Type: 58021- ... D CGLine (SET)

Manufactured by: CEAG