71811- ... D CGLine

Pos.    )		Pcs.

Self-monitoring self-contained luminaire according to EN 60598-1, EN 60598-2-22 and EN 1838 for systems according to EN 50172, DIN VDE 0100-718 and E DIN VDE 0108-100 for separate operation or for connection to the central monitoring device CG-Controller CGLine 400.

If connected to the central monitoring device CG-Controller CGLine 400 a non-screened 2-core bus cable to the luminaire is also needed.

Standard version with:

- Test button

- Test results with fault analysis (lamps, charging and battery circuit) as well as status displays (operation, function test, duration test) via 3 coloured LEDs

- automatic function test (weekly)

- automatic duration test (every 3 months)

- automatic charging monitoring

- deep discharge protection with restart inhibit

- no-load and short-circuit shut down of the inverter 
- manual function test or duration test with test button 
- 1 minute delay of normal mode after mains returns 
- blocking function with CG-Controller CGLine 400 in times of shut-down

Luminous flux (E/(N approx. 40 %

Lamp: incl. fluorescent tube 8 W, T16/450 Im

Emergency lighting rated operating time:

..... 1 h NC rechargeable battery 3.6 V/1.5 Ah

..... 3 h NC rechargeable battery 3.6 V/4.0 Ah

Permitted temperature range:

Maintained light: -5°C to + 30°C

Non-maintained light: 0°C to +35°C

Housing:

Extruded aluminium profile, with mitre cut.

With one-sided light exit and additional light exit at the bottom.

Lamps can be changed without tools.

Insulation class: II; Degree of protection: IP 40

Connection terminals: 2.5 sq mm

Supply voltage: 230V 50Hz

Dimensions (mm): L = 349 H = 188 D = 80

Housing colour: aluminium matt anodised

Plastic cover:

..... clear cover

..... cover with legend (screen printing), viewing distance: 32 m

Luminaires are generally suitable for maintained or non-maintained mode.

Accessories:

..... pcs. wire guard

Type: 78011- ... D CGLine

Manufactured by: CEAG

71821- ... D CGLine WM

Pos.    )		Pcs.

Self-monitoring self-contained luminaire according to EN 60598-1, EN 60598-2-22 and EN 1838 for systems according to EN 50172, DIN VDE 0100-718 and E DIN VDE 0108-100 for separate operation or for connection to the central monitoring device CG-Controller CGLine 400.

If connected to the central monitoring device CG-Controller CGLine 400 a non-screened 2-core bus cable to the luminaire is also needed.

Standard version with:

- Test button

- Test results with fault analysis (lamps, charging and battery circuit) as well as status displays (operation, function test, duration test) via 3 coloured LEDs

- automatic function test (weekly)

- automatic duration test (every 3 months)

- automatic charging monitoring

- deep discharge protection with restart inhibit

- no-load and short-circuit shut down of the inverter 
- manual function test or duration test with test button 
- 1 minute delay of normal mode after mains returns 
- blocking function with CG-Controller CGLine 400 in times of shut-down

Luminour flux (E/(N approx. 40 %

Lamp: incl. fluorescent tube 8 W, T16/450 Im

Emergency lighting rated operating time:

..... 1 h NC rechargeable battery 3.6 V/1.5 Ah

..... 3 h NC rechargeable battery 3.6 V/4.0 Ah

Permitted temperature range:

Maintained light: 5°C to +30°C

Non-maintained light: 0°C to +35°C

Housing:

Extruded aluminium profile, with mitre cut.

For wall mounting.

With two-sided light exit and additional light exit at the bottom.

Lamps can be changed without tools.

Insulation class: II; Degree of protection: IP 40

Connection terminals: 2.5 sq mm

Supply voltage: 230V 50Hz

Dimensions (mm): L = 349 H = 188 D = 80

Housing colour: aluminium matt anodised

Plastic cover:

..... clear cover

..... blind cover

..... cover with legend (screen printing), viewing distance: 32 m

Luminaires are generally suitable for maintained or non-maintained mode.

Accessories:

..... pcs. mounting kit for wall and ceiling mounting

Type: 71821- ... D CGLine WM

Manufactured by: CEAG

71821- ... D CGLine DM

Pos.    )		Pcs.

Self-monitoring self-contained luminaire according to EN 60598-1, EN 60598-2-22 and EN 1838 for systems according to EN 50172, DIN VDE 0100-718 and E DIN VDE 0108-100 for separate operation or for connection to the central monitoring device CG-Controller CGLine 400.

If connected to the central monitoring device CG-Controller CGLine 400 a non-screened 2-core bus cable to the luminaire is also needed.

Standard version with:

- Test button

- Test results with fault analysis (lamps, charging and battery circuit) as well as status displays (operation, function test, duration test) via 3 coloured LEDs

- automatic function test (weekly)

- automatic duration test (every 3 months)

- automatic charging monitoring

- deep discharge protection with restart inhibit

- no-load and short-circuit shut down of the inverter 
- manual function test or duration test with test button 
- 1 minute delay of normal mode after mains returns 
- blocking function with CG-Controller CGLine 400 in times of shut-down

Luminour flux (E/(N approx. 40 %

Lamp: incl. fluorescent tube 8 W, T16/450 Im

Emergency lighting rated operating time:

..... 1 h NC rechargeable battery 3.6 V/1.5 Ah

..... 3 h NC rechargeable battery 3.6 V/4.0 Ah

Permitted temperature range:

Maintained light: 5°C to +30°C

Non-maintained light: 0°C to +35°C

Housing:

Extruded aluminium profile, with mitre cut.

For ceiling mounting.

With two-sided light exit and additional light exit at the bottom.

Lamps can be changed without tools.

Insulation class: II; Degree of protection: IP 40

Connection terminals: 2.5 sq mm

Supply voltage: 230V 50Hz

Dimensions (mm): L = 349 H = 188 D = 80

Housing colour: aluminium matt anodised

Plastic cover:

..... clear cover

..... blind cover

..... cover with legend (screen printing), viewing distance: 32 m

Luminaires are generally suitable for maintained or non-maintained mode.

Accessories:

..... pcs. mounting kit for wall and ceiling mounting

Type: 71821- ... D CGLine DM

Manufactured by: CEAG

71821- ... D CGLine PM

Pos.    )		Pcs.

Self-monitoring self-contained luminaire according to EN 60598-1, EN 60598-2-22 and EN 1838 for systems according to EN 50172, DIN VDE 0100-718 and E DIN VDE 0108-100 for separate operation or for connection to the central monitoring device CG-Controller CGLine 400.

If connected to the central monitoring device CG-Controller CGLine 400 a non-screened 2-core bus cable to the luminaire is also needed.

Standard version with:

- Test button

- Test results with fault analysis (lamps, charging and battery circuit) as well as status displays (operation, function test, duration test) via 3 coloured LEDs

- automatic function test (weekly)

- automatic duration test (every 3 months)

- automatic charging monitoring

- deep discharge protection with restart inhibit

- no-load and short-circuit shut down of the inverter 
- manual function test or duration test with test button 
- 1 minute delay of normal mode after mains returns 
- blocking function with CG-Controller CGLine 400 in times of shut-down

Luminour flux (E/(N approx. 40 %

Lamp: incl. fluorescent tube 8 W, T16/450 Im

Emergency lighting rated operating time:

..... 1 h NC rechargeable battery 3.6 V/1.5 Ah

..... 3 h NC rechargeable battery 3.6 V/4.0 Ah

Permitted temperature range:

Maintained light: 5°C to +30°C

Non-maintained light: 0°C to +35°C

Housing:

Extruded aluminium profile, with mitre cut.

For pendulum mounting.

With two-sided light exit and additional light exit at the bottom.

Lamps can be changed without tools.

Insulation class: II; Degree of protection: IP 40

Connection terminals: 2.5 sq mm

Supply voltage: 230V 50Hz

Dimensions (mm): L = 349 H = 188 D = 80

Housing colour: aluminium matt anodised

Plastic cover:

..... clear cover

..... blind cover

..... cover with legend (screen printing), viewing distance: 32 m

Luminaires are generally suitable for maintained or non-maintained mode.

Accessories:

..... pcs. pendulum mounting set 0.5m

..... pcs. pendulum mounting set 1.0m

..... pcs. pendulum mounting set 1.5m

..... pcs. chain fastening

Type: 71821- ... D CGLine PM

Manufactured by: CEAG