8811- ... D CGLine

Pos.    )		Pcs.

Self-monitoring self-contained luminaire pursuant to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems pursuant to DIN VDE 0108 / 10.89 for separate operation or for connection to the central monitoring device CG-Controller CGLine 400.

If connected to the central monitoring device CG-Controller CGLine 400 a non-screened 2-core bus cable to the luminaire is also needed.

Standard version with:

- Test button

- Test results with fault analysis (lamps, charging and battery circuit) as well as status displays (operation, function test, duration test) via 3 coloured LEDs

- automatic function test (weekly)

- automatic duration test (every 3 months)

- automatic charging monitoring

- deep discharge protection with restart inhibit

– no-load and short-circuit shut down of the inverter

Luminous flux E/N approx. 40 %

Lamp: incl. fluorescent tube 8 W, T16/450 Im

Emergency lighting rated operating time:

..... 1 h NC rechargeable battery 3.6 V/1.5 Ah

..... 3 h NC rechargeable battery 3.6 V/4.0 Ah

Permitted temperature range:

Maintained light: -5°C to + 30°C

Non-maintained light: 0°C to +35°C

Housing:

Ceiling installation housing made of sheet steel, bezel painted in RAL 9010.

Structured cover made of plastic. For ceiling thickness of up to 40 mm.

Insulation class: I; degree of protection: IP 20

Connection terminals: 2.5 sq mm

Supply voltage: 230V 50Hz

Dimensions (mm): L = 360. H = 127. D = 105

Housing colour: white

Luminaires are generally suitable for maintained or non-maintained mode.

Type: 8811- ... D CGLine

Manufactured by: CEAG