Pos.    )		... pcs.

V-CG-SLU 700

LED Supply- and Monitoring module acc. to EN 61347-2-13 and EN 62384 with 20 addresses for function monitoring (CEWA GUARD Technology) of a LED series connection (1-4 LEDs, 700mA) - without additional data line. Error message in case of: Interruption in the LED series connection or a short circuit at the output terminals.

Suitable to be mounted in luminaires of insulation class I or II for emergency lighting acc. to EN 60598-2-22 and for the operation in emergency lighting systems acc. to DIN VDE 0100-718, DIN EN 50172 and DIN V VDE V 0108-100.

Acc. to ISO 9001 developed, manufactured and tested.

With ENEC-compliance, certified by an independent testing laboratory.

Switching modes (maintained/non-maintained and switched emergency luminaires) freely programmable in one circuit without additional data line to the luminaires in conjunction with suitable emergency lighting systems (with STAR-Technology).

Primary side:

Voltage:			220 - 240 V, 50/60 Hz /176 - 275 V DC

Standby power loss:		< 0.7 W (230 V / 50 Hz)

Current input:			93mA (230V AC) / 56mA (220V DC)

Power Input:			21.4 VA (230V AC)

Inrush current:			≤ 3,0A

Connecting terminals:		Plug-in terminals 2.5 mm² / reverse-polarity protected

Secondary side:

Output current:			700mA (constant current)

Output voltage:			14V DC (open-circuit operation)

Lamp load:			LED series connection (1-4 LEDs; rated current 700mA;

UFmin = 2.9V / UFmax = 3.5V per LED)

Output power:			9.8W (max.)

Connecting terminals:		Plug-in terminals 1.5 mm² / not reverse-polarity protected

Max. distance

Module / LED:			1 m

Degree of protection:		IP 20

Ambient

temperature range ta:		-20°C up to +50°C

Max. permissible

test point temperature tc:	70°C

Dimensions (mm): 		H = 21; L = 139; W = 30

Enclosure material / colour:	flame-retardant polycarbonate / grey

Type: V-CG-SLU 700

Manufactured by: CEAG