Pos.    )		... pcs.

V-CG-S 4–400W

Emergency luminaire monitoring module acc. to EN 61347-2-11 and EN 60669-2-1 with 20 addresses for function monitoring (CEWA GUARD Technology) of loads between 4-400 W (fluorescent lamps with high frequency electronic ballast, tungsten halogen lamps with electronic transformer and incandescent lamps) in DC-operation without additional data line.

Suitable to be mounted in luminaires of insulation class I or II for emergency luminaires acc. to EN 60598-2-22 and for the operation in emergency lighting systems acc. to DIN VDE 0100-718, DIN EN 50172 and E DIN VDE 0108-100.

Acc. to ISO 9001 developed, manufactured and tested.

With ENEC-compliance, certified by an independent testing laboratory.

Switching modes (maintained/non-maintained and switched emergency luminaires) freely programmable in one circuit without additional data line to the luminaires in conjunction with suitable emergency lighting systems (with STAR-Technology).

Voltage:			220 – 240 V, 50/60 Hz /176 – 275 V DC

Standby power loss:		< 0.5 W (230 V / 50 Hz)

Power Input:			Lamp 4 – 400 W

Max. distance

Luminaire / V-CG-S:		500 m

Degree of protection:		IP 20

Permissible

temperature range ta:		-20°C to +60°C

Max. permissible

test point temperature tc:	75°C

Connection terminals:		plug terminals 1.5 mm², mains connection reverse polarity protection

Dimensions (mm): 		H = 21; L = 85; W = 30

Fitting position:			horizontal or sidewise upright

Enclosure material:		flame-retardant polycarbonate

Type: V-CG-S 4–400W

Manufactured by: CEAG