Pos.    )		... pcs.

V-CG-SB

Emergency luminaire monitoring module acc. to EN 61347-2-11 and EN 60929 Annex E with 20 addresses for function monitoring (CEWA GUARD Technology) of a single lamp DALI control gear in DC-operation. Without additional data line to the emergency power supply system.

Suitable to be mounted in luminaires of insulation class I or II for emergency luminaires acc. to EN 60598-2-22 and for the operation in emergency lighting systems acc. to DIN VDE 0100-718, DIN EN 50172 and E DIN VDE 0108-100.

Safe galvanic isolation of the bus systems (emergency lighting / mains lighting) during emergency operation acc. E DIN VDE 0108-100 (08/2007).

Acc. to ISO 9001 developed, manufactured and tested.

With ENEC-compliance, certified by an independent testing laboratory.

Qualified for the integration into a luminaire of a DALI light - management – system as an emergency luminaire in a CEAG emergency lighting system with STAR – Technology.

Without integration into a DALI light - management – system:

Switching modes (maintained/non-maintained and switched emergency luminaires) freely programmable in one circuit in conjunction with suitable emergency lighting systems (with STAR-Technology).

Adjustable luminous flux relation in DC mode in 10% steps between 10% and 100%.

Voltage:			220 – 240 V, 50/60 Hz /176 – 275 V DC

Standby power loss:		< 0.5 W (230 V / 50 Hz)

Connection:			single lamp DALI lamp control gear

Max. distance

DALI ECG / V-CG-SB:		1 m

Degree of protection:		IP 20

Permissible

Temperature range ta:		-20°C to +60°C

Max. permissible

test point temperature tc:	65°C

Connection terminals mains:	plug-in terminals 2.5 mm²,

mains connection reverse polarity protection

Connection terminals DALI bus:	plug-in terminals 1.5 mm²,

Dimensions (mm): 		H = 21; L = 145; W = 30

Fitting position:			horizontal or sidewise upright

Enclosure material:		flame-retardant polycarbonate

Type: V-CG-SB

Manufactured by: CEAG